## Criteria Level 2&3
STANDARDS FOR THE DESIGN OF CONTAINMENT LEVEL 2 LABORATORIES AT UNIVERSITY OF NOTTINGHAM
Abbreviations
CZ | Containment zone - this may be a single lab or a suite of rooms with a defined boundary | Additional requirements for CL facilites are shown in red font.
UBSA | University Biosafety Adviser
MSC | MICROBIOLOGICAL SAFETY CABINETS [MSC]
FC | Fume cupboard
ACTSA | Anti Terrorism Crime & Security Act
CIBSE | Chartered Institute of Building Services Engineers
MINIMUM REQUIREMENTS |  | HOW CRITERIA WILL BE MET IN DESIGN | CONFIRMATION CRITERIA MET ON COMPLETION
BASIC DESIGN
1 | Security & Access
1.1 | Access to be limited to authorised persons only be use of security measures such as locks for controlling entry
1.2 | Security provisions must meet Home Office standards for labs holding specified materials controlled under ACTSA 2001. Local School/department safety officer and UBSA to identify if relevant.
1.3 | Access restriction to be imposed at entrace to the CZ
Additional requirements for CL3 laboratories:
1.4 | Access to CL3 zone to be restricted either by swipe card, card key or digital lock
1.5 | Automatic door closures to be fitted to ensure CL3 zone is secure even whilst occupied.
1.6 | Containment zone to remain secure in event of fire alarm activation in order to maintain biosecurity - locks not to be automatically opened - emergency release mechanisms to be installed to allow egress at any time.
1.7 | Security provisions to meet Home Office standards for laboratories holding materials controlled under anti terrorism legislation.
2 | Building services
2.1 | Controls and services should be outside the containment zone
2.2 | Need for maintenance staff to enter CZ to be minimised.
2.3 | Access to service risers to be from outside CZ wherever possible
Additional requirements for CL3 laboratories:
2.4 | The need for maintenance staff to enter the containment zone tobe eliminated. Services should not require maintenance from within the containment zone if this can be reasonably provided outside. All service access requirements to be listed by designer and agreed by the University Biological Safety Adviser.
2.5 | Gas cylinders to be located outside the CL3 containment zone and piped in.
3 | Space requirements
3.1 | Sufficient space to be allowed for staff to carry out work safely.
University Space Requirement Standards can be found at http://www.nottingham.ac.uk/estate/docs/space_allocation_guidelines.pdf
Management, Design & Operation of Microbiological Containment Labs states 2.4 cu meter[ based on nominal ceiling ht of 2.4m = 10sq m]
3.2 | Layout of benches and furniture to be in accordance with BS EN 14056
3.3 | Location and space requirements for Microbiological Safety Cabinets [MSC] & Fume Cupboards [FC]] to be in accordance with appropriate British Standard
3.4 | Ceiling height and entrance doors must allow sufficient headroom/space to accommodate installation, replacement and maintenance of large equipment and access to ductwork above MSCs & FCs [ min 300mm above these]
4 | Transport, storage and traffic routes [ movement of lab personnel & materials between lab areas and facilities]
4.1 | CZs to be self contained as far as possible. Labs to be connected to ancillary support facilities such as centrifuge rooms/ autoclaves
4.2 | Traffic routes to and from central services such as wash up and autoclave not to be through office, public or food serving areas.
4.3 | Lift access to be provided for trolleys if laboratory items have to be moved between floors. 'Clean' & 'dirty' traffic routes to be carefully considered in regard to use of lifts.
4.4 | Clear segregation of lab coat and non-lab coat routes and zones.
Additional requirements for CL3 laboratories:
CL3 containment zone to be separated from other activities in the same building by use of a lobby area - lobby to be within the curtilage of the CL3 containment zone - lobby to be used for changing of labcoats and handwashing - lobby doors to be interlocked - lobby doors to be offset (not opposite each other).
Fire exit routes from other areas not to require travel through CL3 containment zone.
The CL3 laboratory to contain all its own equipment to minimize infectious material having to be taken outside for any purpose - all storage of infectious materials to be within CL3 suite ideally the lab, or lobby or if this is not practicable then within a CL3 facility nearby).
5 | Write up space and offices
5.1 | Laboratories to have a dedicated space to allow occupants to carry out essential write up tasks and store essential notes. This should not be part of a general lab bench and should be clearly segregated from the lab area.
5.2 | Offices and meeting rooms where carpeting /soft furnishings are required or where eating /drinking may take place must be sited outside the CZ. Rooms opening off the containment lab is not acceptable.
6 | Storage of outdoor garments and personal items
6.1 | Outdoor clothing personal items must not be taken into lab.
6.2 | Adequate provision of secure storage, taking into account number of people working in the lab, must be made outside the CZ.
GENERAL STRUCTURE, FURNITURE AND FINISHES
7 | Benches
7.1 | Layout of benches and furniture to be in accordance with BS EN 14056
7.2 | Surfaces resistant to acids, alkalis, solvents and disinfectants expected in normal use, and impervious to water and easy to clean
Solid plastic laminate [ e.g. Trespa] or epoxy
Not scribed to the wall - to have upstand/backplate
Minimal joints and seams but where necessary to be sealed with non shrinking sealant [ e.g. two part epoxy grout]
No open holes for feeding cables
Drip cups to be avoided
To be sufficiently robust and supported underneath to accommodate safely any heavy items of equipment
8 | Furniture
8.1 | Adequate amount of under and over bench storage
8.2 | Laminate covered MDF adequate for shelves/cupboard fronts
8.3 | Shelving to be of sufficient strength in terms of materials and fixings to accommodate items identified by discussion with end user.
8.4 | Shelving over lab benches to be at a height that allows safe access without use of stool and designed so that items cannot fall off the other side
8.5 | Under bench cupboards to be designed to allow easy access for cleaning of any spillage.
9 | Sinks
9.1 | Labs will require general purpose sinks - number to be determined following discussion with end user.
Waste pipes and drains to be of suitable materials resistant to substances likley to enter drain system
Waste to run directly to drain
Epoxy/ steel all in one units preferred.
Seals round sinks to be ain accordance with 7.2 above
Note - if radioactive materials are to be used in the area there will be specific drainage requirements not covered by this standard.
10 | Hand wash basins
10.1 | Dedicated HWB to be located at each exit to CZ
10.2 | Tissue culture/microbiological labs within theCZ will require additional HWB at exit
10.3 | Taps to be of type that can be operated without being touched by hand. [elbow, automatic sensor. Knee operated]
10.5 | Dispenser for soap and paper towel adjacent to sink.
10.6 | Soap dispenser to use single use packs
11 | Eye wash/first aid
11.1 | Eye wash station to be adjacent to HWB - type to be determined by risk assessment by end user.
For low risk situations 2X 500 ml sterile eye wash bottles acceptable.
11.2 | Drench showers are unlikely to be required unless significant volumes of corrosive chemicals will be used.]
11.3 | First aid kit to be located close to HWB - size dependant on number of occupants.
12 | Lab coat storage
12.1 | Separate storage area for lab coats in use.
Must be within the CZ adjacent to HWB [ coats not acceptable on corridors]
Sufficient number of pegs to ensure only one coat per hook
Additional requirements for CL3 laboratories:
12.2 | Facilities for storage of labcoats to be provided in the lobby(separate storage required for clean coats and those in use).
12.3 | If the CL3 laboratory is located within a larger containment zone then pegs to be provided outside the CL3 zone for storage of labcoats from the CL2 area.
13 | Floors
13.1 | Surfaces resistant to acids, alkalis, solvents and disinfectants expected in normal use, and impervious to water and easy to clean
seams to be kept to a minimum, where necessary to be sealed.
easy to keep clean - not of none slip type unless specific requirements for wet are
coved to wall and sealed [ sit on coving not acceptable]
13.2 | Alternative material /protection to be provided to areas where liquid nitrogen dispensed.
13.3 | No open floor drains within CZ or ancillary support areas.
13.4 | No access hatches in floor coverings.
14 | Doors & windows
14.1 | Vision panel in door
14.2 | Doors at entrance to the CZ to be self closing
14.3 | Windows fire resistant and double glazed - designed to allow safe access whilst cleaning
14.4 | Blinds to not collect dust [ vertical or similar ]
Additional requirements for CL3 laboratories:
Doors to open into the CL3 space and have leakage through grill or round edges in order to maintain inward airflow and minimise disruptions to airflow patterns during use.
The CL3 laboratory to have observation window(s) so - occupants can be seen wherever they are within the laboratory from outside - any fire detector activation can be visually checked.
Blinds ideally to be located between the window panes or where installed in the laboratory to be made of a non-absorbent material.
Fire resistant, double glazed windows must be provided for both security and containment purposes. These to be sealed in place, flush on the containment faces and edges with the adjacent walls.
15 | Walls & ceilings
15.1 | Smooth and easily cleaned
Additional requirements for CL3 laboratories:
See section 5 on fumigation which includes criteria for walls and ceilings.
16 | Lighting
16.1 | Standard light fittings positioned to avoid shadows over work surfaces.
16.2 | Light levels to be in accordance with CIBSE guide - minimum 500lux - in some areas 1000 lux may be appropriate. Such as to avoid need for task lighting.
Additional requirements for CL3 laboratories:
16.3 | Standard (general purpose) light fittings adequate - light fittings to be suspended or surface mounted with minimal ingress into ceiling and visible seal (recessed fittings not acceptable).
16.4 | Non-maintained emergency lighting to be provided in all CL3 areas adequate to enable staff to make work safe under power loss conditions.
17 | Power/data
17.1 | Standard outlet sockets acceptable for lab areas, areas such as cold rooms will required specific type
17.2 | Location of sockets to be such as to be away from any source of water contamination
17.3 | Adequate numbers of data and electrical points [ as defined by end user] both under and over bench to avoid trailing cables and use of multi adapters
Additional requirements for CL3 laboratories:
Adequate telephone and data points to be provided for - e-mail or fax to be used to remove written information from laboratory (to obviate need for decontaminating paper) - hands free telephone to be installed.
UPS supply to be fitted to ensure door access control and extract /supply air systems continue to operate for minimum of 1hr to enable staff to make work safe and exit laboratory under power loss conditions.
18 | WASTE MANAGEMENT
18.1 | Autoclave to be available for decontamination of waste
To be located in the building
Conform to BS 2646 & BS EN 12347
to have adequate space adjacent for storage and handling of waste
to have adequate space to allow safe access for maintenance and service engineers
to have adequate ventilation to prevent build up of heat /smells
18.2 | If liquid waste generated at end of cycle a sluice will be required adjacent to autoclave
18.3 | Storage of waste pending removal - secure location and adequate space to accommodate waste pending removal by contractor.
Additional requirements for CL3 laboratories:
18.4 | A dedicated autoclave to be sited within the CL3 containment zone, - to be ensured heat output does not effect airflows (carefully consider positioning of autoclave) - if double ended/pass through autoclave installed to have effective and appropriate sealing to maintain integrity of containment zone .
18.5 | Installation of autoclave to include measures to ensure there is no discharge of potentially contaminated material via air vents or condensate during use.
18.6 | Position of discharge vents to be away from supply air intake vents
19 | MICROBIOLOGICAL SAFETY CABINETS [MSC]
19.1 | Where needed agree appropriate Class with end users and UBSA
19.2 | Cabinets to comply with BS EN 12469
19.3 | Agree shortlist of acceptable suppliers in consultation with end user, UBSA & Estates
19.4 | Cabinets to be sited in accordance with BS 5726 2005. Must not be affected by ventilation and air con units.
19.5 | Ideally MSC to be ducted to atmosphere - if recirculating models have to be used then must have double HEPA filters on exhaust.
19.6 | Consideration to be given at the design stage to the means of fumigating MSCs. Where possible use of Vaporised Hydrogen peroxide preferred. Consult UBSA for advice.
19.7 | Cabinets to be commissioned and certified as passing operator protection factor test [OPF > 1x105] prior to handover , witnessed by competent person
Additional requirements for CL3 laboratories:
19.8 | At least one safety cabinet to be installed - Class to be agreed by University Biological Safety Adviser.
19.9 | Safety cabinet(s) to extract direct to atmosphere and be hard ducted (thimble systems or recirculating cabinets are not acceptable at Containment Level 3).
20 | Fumigation
20.1 | There is no requirement to fumigate CL2 laboratories.
Additional requirements for CL3 laboratories:
20.2 | CL3 containment zone to be of totally sealed construction and require minimal manual external sealing to permit fumigationwithout loss of fumigant - boundary of room to be obvious and clearly visible. Ceiling voids are not to be within the sealed boundary, boxing in of services to be avoided - ceiling to be solid or continuous and coved to walls, detailing to ensure no cracking at joints - walls and ceiling to be seamless/jointless - any penetrations in ceilings, walls and floors - to be kept to a minimum - to be totally sealed using proprietary fittings (eg IP68 rated glands for electrics and pipework) - electrical and conduit services to be sealed - all sealants to be resistant to formaldehyde and be non-hardening - particular attention to be paid to sealing of hidden penetrations eg behind sockets.
20.3 | Fumigation strategy and procedures, including the rationale for fumigation of different areas vs whole suite, to be agreed in consultation with the appropriate School representatives andthe University Biological Safety Adviser. Careful consideration must be given to substitution with a safer alternative e.g. VHP
20.4 | Electric swtich points for generation of fumigant to be located external to the CL 3 suite.
20.5 | Air handling system to be operable from outside the suite to allow venting of fumigant without entering lab.
20.6 | A port must be provided in the laboratory door/lobby door to allo insertion of gas meter probe. Port must be fully sealed screw capped and fitted with 'o' ring. Approx 1 meter off ground.
21 | VENTILATION
21.1 | Acceptable maximum temperatures within recognised standards to be specified by School representatives in consultation with Estates. [ See CIBSE guide]
21.2 | If CZ is mechanically ventilated there must be an inward flow of air from adjacent areas into the CL. This may be achieved by extract volume removing great volume of air that delivered [ e.g. supply 90% of extract]
21.3 | CZ must not become positively pressured with respect to surrounding areas. Extract systems to be interlocked to supply system to prevent supply system operating in event of extract failure
21.4 | Supply inlets and extract points to be positioned
to ensure maximum mixing and dilution
to avoid compromising performance of MSCs & FCs
21.5 | All air extracted from CZ to be exhausted direct to atmosphere. Location of extract terminal to be such that there is no recirculation of extracted air into the supply system.
Additional requirements for CL3 laboratories:
21.6 | Ventilation system design to be as simple as possible and include provisions for fumigation procedures. Fumigation procedures to take account of whether there is a need to fumigate rooms individually or whether the suite is fumigated as a whole. In the case of individual room fumigation, capability also to take account of whether the rest of the suite is to remain operational or is shut down.
21.7 | There is to be a continuous inward airflow into the laboratory - ascertain in consultation with University Biological Safety Adviser whether this is required at all times or only when work is in progress - to be ensured upper and lower limit errors on supply and extract do not overlap - potential effects of operation of ventilation system in other parts building to be taken into account (changes overnight etc).
21.8 | In order to ensure adequate Laboratory Protection Factor isachieved and containment is maintained when the door isopened there is to be air inflow through the doorway (criticalsafety requirement) - design to include air being drawn passively through the door under normal operating conditions (eg gaps around and grilles in doors) - inflow of at least 103 m3/min (0.17 m3/sec) required through the door - air change rates to be discussed and agreed with Estates and Building Project Manager (energy costs issues) and the University Biological Safety Adviser (safety issues).
21.9 | A negative pressure differential between CL3 laboratory and the immediately adjacent space across the containment barrier of at least –30Pa to be achieved by ducting the exhaust air from the microbiological safety cabinet(s) (and any bypass) to the outside air through a HEPA filter, and where this does not provide adequate pressure differential to also extract the laboratory air through independent ducting to the outside airthrough a HEPA filter.
21.1 | Where there are inner rooms there is to be a pressure cascade with a differential pressure of at least -15Pa between areas - all pressures and controls to be referenced to outside the CL3 containment barrier.
21.11 | All controls and access to all parts of the ventilation system to be provided outside the CL3 zone in order these can be operated and maintained without entering the CL3 zone - controls to be tamper proof to prevent unauthorised adjustment - controls for ventilation system also require to be located outside the laboratory to enable remote operation during fumigation procedures.
21.12 | A magnahelic gauge to show the CL3 zone is operating at negative pressures to be installed at the entrance to each innerroom and at the entrance to the CL3 zone. Normal operating parameters to be clearly indicated on, or immediately adjacent to, all gauges. If pressures rise above design tolerances an audible alarm to sound - accuracy of magnahelic gauges to be confirmed by calibration.
21.13 | A fumigation panel is to be provided that indicates status of the ventilation system during fumigation.
21.14 | Exhaust of ventilation system to extract direct to atmosphere, ideally at roof level, and be dedicated to the CL3 laboratory or CL3 suite.
21.15 | Extract fan to be at terminal point of ductwork (i.e. downstream of HEPA filters
21.16 | All extract air systems must have HEPA filter installed - HEPA filters to meet performance criteria of class H14 filter as defined in BS EN 1822-1: 1998. - test ports to be provided both sides of all HEPA filters to allow checks to confirm filter integrity/performance.
21.17 | Means of preventing reverse air flows to be incorporated into the system.
21.18 | In the event of extract fan failure, the input supply air is to be cut off as soon as possible to prevent any positive pressurisation of the CL3 laboratory - to be hard wiring between extract and input fans rather than routed through BMS.
21.19 | Extract fan failure to be indicated by an audible alarm that can be heard throughout the inside and immediately outside the CL3 zone. Alarm activation may be through BMS.
21.2 | Dampers, mechanical or electrical, to be provided to seal the CL3 zone for fumigation - all dampers to be located where they can be visually inspected to check they are working (vision panels to be provided) - test ports to be provided either side of all dampers to allow checks to confirm dampers are closing fully - dampers to be sited as near as possible to the CL3 containment line but to be accessed from outside the containment zone for service and maintenance
21.21 | No joints or welds to be located in any duct or pipework passing above the ceiling of the CL3 zone.
21.22 | Where cabinets have by-pass systems these to operate to minimise any change in laboratory negative pressure on switch over.
21.23 | Lobby to be part of the CL3 containment zone.
21.6 | The ventilation system to continue to run in the event of fire alarm activation with provision for manual shut down by fire brigade.
21.21 | The Designer of the ventilation system is to provide a summary of the operation of the ventilation system which is to be agreed in principle with the University Biological Safety Adviser. This is to be provided and confirmed prior top handover of the facility. This summary is also to be provided to the users as part of the familiarisation and training process prior to handover. It should be a simple summary that is written in layman’s terms in order that it can be understood by users and other non-specialist (i.e. not engineer) persons. It is to include a description of - how air is supplied - how air is extracted and where the fan and HEPA filters are located - what happens when the safety cabinets are switched on and off - how cabinet performance is linked to the ventilation system - where the line of containment is - where the various dampers are to isolate the CL3 zone - where the controls are and what they operate - what the normal operating parameters are in order that any deviations can be recognised - basis for fumigation procedures, including a clear statement on what the ventilation system design allows in terms of either individual room or whole suite fumigation and how the ventilation system works to allow these or not as the case may be - how to carry out the fumigation procedure including what to do to seal the laboratory for fumigation, how to clear the fumigant afterwards using the ventilation system and how to restart and check the ventilation system is operating within design parameters. This is to be supported by a simple flow chart or check list detailing the precise sequence of events and include approximate time lags for each stage and what readings should be shown on the various gauges.
22 | VALIDATION
22.1 | Architect to confirm that all aspects of this specification that have been included in the design of the building have met deign criteria on installation
22.2 | Contractor to provide commissioning data to confirm ventilation system operated in accordance with the design specification.
22.3 | Independent certification required to demonstrate performance to the BS of
Autoclaves
Macs
FRCS
Any other specified equipment
To be witnessed by a competent representative of the School /University
Additional requirements for CL3 laboratories:
22.4 | Pressure regime to be tested against design specification.
22.5 | Interlock between extract and supply air systems to be proven to ensure that supply air system cannot operate in the event of failure of the extract system(s).
22.6 | Laboratory to be run at maximum operating negative pressure and it be checked that no damage is caused to fabric and services.
22.7 | All air supply and extract ductwork to be pressure tested in situ for air tightness.
22.8 | Dampers and seals to be checked in situ for air tightness.
22.9 | All seals around windows, pipework, electrics etc, joints of walls, ceilings etc, any trunking, ductwork etc, to be checked visually and locally smoke tested (looking for any air movements with smoke tubes) under static pressure - to be in accordance with procedures in HSE publication Sealability of Microbiological Containment Level 3 and 4 Facilities. ACDP. 2006 (available as web only document at http://www.hse.gov.uk/biosafety/gmo/guidance/se alability.pdf).
22.1 | Where necessary, the contractor to carry out any further tests (prior to test fumigation see 22.15 below) to be confident as to the sealability of the CL3 areas to permit fumigation and prevent escape of fumigant. Guidance on procedures as in 22.9 above.
22.11 | Any HEPA filters in room extract system to be tested against specification (current British Standard) and that filter housings are air tight.
22.12 | All alarm systems to be checked and tested.
22.13 | All ventilation system controls to be tested and commissioned under operational conditions, to include - start up - shut down - room fumigation procedures - simulated failure scenarios (all possible failures for the particular system) - routine running.
22.14 | All workings of the ventilation system, in particular the control systems, to be explained and demonstrated to users.
22.15 | Where indicated as required by the risk assessment a test fumigation to be carried out by an appointed contractor assisted by the University after all other commissioning tests and validation shown to be satisfactory but prior to handover. The test fumigation must be successful as indicated by no leakage of fumigant and acceptable level of kill (>105 log reduction) on test spore strips. Local safety officer /CL3 suite manager to oversee fumigation procedures and agree successful.

## Criteria Level 2
STANDARDS FOR THE DESIGN OF CONTAINMENT LEVEL 2 LABORATORIES AT UNIVERSITY OF NOTTINGHAM
Abbreviations
CZ | Containment zone - this may be a single lab or a suite of rooms with a defined boundary
UBSA | University Biosafety Adviser
MSC | MICROBIOLOGICAL SAFETY CABINETS [MSC]
FC | Fume cupboard
ACTSA | Anti Terrorism Crime & Security Act
CIBSE | Chartered Institute of Building Services Engineers
MINIMUM REQUIREMENTS |  | HOW CRITERIA WILL BE MET IN DESIGN | CONFIRMATION CRITERIA MET ON COMPLETION
BASIC DESIGN
1 | Security & Access
1.1 | Access to be limited to authorised persons only be use of security measures such as locks for controlling entry
1.2 | Security provisions must meet Home Office standards for labs holding specified materials controlled under ACTSA 2001. Local School/department safety officer and UBSA to identify if relevant.
1.3 | Access restriction to be imposed at entrace to the CZ
2 | Building services
2.1 | Controls and services should be outside the containment zone
2.2 | Need for maintenance staff to enter CZ to be minimised.
2.3 | Access to service risers to be from outside CZ wherever possible
3 | Space requirements
3.1 | Sufficient space to be allowed for staff to carry out work safely.
University Space Requirement Standards can be found at http://www.nottingham.ac.uk/estate/docs/space_allocation_guidelines.pdf
Management, Design & Operation of Microbiological Containment Labs states 2.4 cu meter[ based on nominal ceiling ht of 2.4m = 10sq m]
3.2 | Layout of benches and furniture to be in accordance with BS EN 14056
3.3 | Location and space requirements for Microbiological Safety Cabinets [MSC] & Fume Cupboards [FC]] to be in accordance with appropriate British Standard
3.4 | Ceiling height and entrance doors must allow sufficient headroom/space to accommodate installation, replacement and maintenance of large equipment and access to ductwork above MSCs & FCs [ min 300mm above these]
4 | Traffic routes [ movement of lab personnel & materials between lab areas and facilities]
4.1 | CZs to be self contained as far as possible. Labs to be connected to ancillary support facilities such as centrifuge rooms/ autoclaves
4.2 | Traffic routes to and from central services such as wash up and autoclave not to be through office, public or food serving areas.
4.3 | Lift access to be provided for trolleys if laboratory items have to be moved between floors. 'Clean' & 'dirty' traffic routes to be carefully considered in regard to use of lifts.
4.4 | Clear segregation of lab coat and non-lab coat routes and zones.
5 | Write up space and offices
5.1 | Laboratories to have a dedicated space to allow occupants to carry out essential write up tasks and store essential notes. This should not be part of a general lab bench and should be clearly segregated from the lab area.
5.2 | Offices and meeting rooms where carpeting /soft furnishings are required or where eating /drinking may take place must be sited outside the CZ. Rooms opening off the containment lab is not acceptable.
6 | Storage of outdoor garments and personal items
6.1 | Outdoor clothing personal items must not be taken into lab.
6.2 | Adequate provision of secure storage, taking into account number of people working in the lab, must be made outside the CZ.
GENERAL STRUCTURE, FURNITURE AND FINISHES
7 | Benches
7.1 | Layout of benches and furniture to be in accordance with BS EN 14056
7.2 | Surfaces resistant to acids, alkalis, solvents and disinfectants expected in normal use, and impervious to water and easy to clean
Solid plastic laminate [ e.g. Trespa] or epoxy
Not scribed to the wall - to have upstand/backplate
Minimal joints and seams but where necessary to be sealed with non shrinking sealant [ e.g. two part epoxy grout]
No open holes for feeding cables
Drip cups to be avoided
To be sufficiently robust and supported underneath to accommodate safely any heavy items of equipment
8 | Furniture
8.1 | Adequate amount of under and over bench storage
8.2 | Laminate covered MDF adequate for shelves/cupboard fronts
8.3 | Shelving to be of sufficient strength in terms of materials and fixings to accommodate items identified by discussion with end user.
8.4 | Shelving over lab benches to be at a height that allows safe access without use of stool and designed so that items cannot fall off the other side
8.5 | Under bench cupboards to be designed to allow easy access for cleaning of any spillage.
9 | Sinks
9.1 | Labs will require general purpose sinks - number to be determined following discussion with end user.
Waste pipes and drains to be of suitable materials resistant to substances likley to enter drain system
Waste to run directly to drain
Epoxy/ steel all in one units preferred.
Seals round sinks to be ain accordance with 7.2 above
Note - if radioactive materials are to be used in the area there will be specific drainage requirements not covered by this standard.
10 | Hand wash basins
10.1 | Dedicated HWB to be located at each exit to CZ
10.2 | Tissue culture/microbiological labs within theCZ will require additional HWB at exit
10.3 | Taps to be of type that can be operated without being touched by hand. [elbow, automatic sensor. Knee operated]
10.5 | Dispenser for soap and paper towel adjacent to sink.
10.6 | Soap dispenser to use single use packs
11 | Eye wash/first aid
11.1 | Eye wash station to be adjacent to HWB - type to be determined by risk assessment by end user.
For low risk situations 2X 500 ml sterile eye wash bottles acceptable.
11.2 | Drench showers are unlikely to be required unless significant volumes of corrosive chemicals will be used.]
11.3 | First aid kit to be located close to HWB - size dependant on number of occupants.
12 | Lab coat storage
12.1 | Separate storage area for lab coats in use.
Must be within the CZ adjacent to HWB [ coats not acceptable on corridors]
Sufficient number of pegs to ensure only one coat per hook
13 | Floors
13.1 | Surfaces resistant to acids, alkalis, solvents and disinfectants expected in normal use, and impervious to water and easy to clean
seams to be kept to a minimum, where necessary to be sealed.
easy to keep clean - not of none slip type unless specific requirements for wet are
coved to wall and sealed [ sit on coving not acceptable]
13.2 | Alternative material /protection to be provided to areas where liquid nitrogen dispensed.
13.3 | No open floor drains within CZ or ancillary support areas.
13.4 | No access hatches in floor coverings.
14 | Doors & windows
14.1 | Vision panel in door
14.2 | Doors at entrance to the CZ to be self closing
14.3 | Windows fire resistant and double glazed - designed to allow safe access whilst cleaning
14.4 | Blinds to not collect dust [ vertical or similar ]
To be enclosed within pane or alternatively of none absorbent material
15 | Walls & ceilings
15.1 | Smooth and easily cleaned
16 | Lighting
16.1 | Standard light fittings positioned to avoid shadows over work surfaces.
16.2 | Light levels to be in accordance with CIBSE guide - minimum 500lux - in some areas 1000 lux may be appropriate. Such as to avoid need for task lighting.
17 | Power/data
17.1 | Standard outlet sockets acceptable for lab areas, areas such as cold rooms will required specific type
17.2 | Adequate numbers of data and electrical points [ as defined by end user] both under and over bench to avoid trailing cables and use of multi adapters
17.3 | Location of sockets to be such as to be away from any source of water contamination
18 | WASTE MANAGEMENT
18.1 | Autoclave to be available for decontamination of waste
To be located in the building
Conform to BS 2646 & BS EN 12347
to have adequate space adjacent for storage and handling of waste
to have adequate space to allow safe access for maintenance and service engineers
to have adequate ventilation to prevent build up of heat /smells
18.2 | If liquid waste generated at end of cycle a sluice will be required adjacent to autoclave
18.3 | Storage of waste pending removal - secure location and adequate space to accommodate waste pending removal by contractor.
19 | MICROBIOLOGICAL SAFETY CABINETS [MSC]
19.1 | Where needed agree appropriate Class with end users and UBSA
19.2 | Cabinets to comply with BS EN 12469
19.3 | Agree shortlist of acceptable suppliers in consultation with end user, UBSA & Estates
19.4 | Cabinets to be sited in accordance with BS 5726 2005. Must not be affected by ventilation and air con units.
19.5 | Ideally MSC to be ducted to atmosphere - if recirculating models have to be used then must have double HEPA filters on exhaust.
19.6 | Consideration to be given at the design stage to the means of fumigating MSCs. Where possible use of Vaporised Hydrogen peroxide preferred. Consult UBSA for advice.
19.7 | Cabinets to be commissioned and certified as passing operator protection factor test [OPF > 1x105] prior to handover , witnessed by competent person
20 | VENTILATION
20.1 | Acceptable maximum temperatures within recognised standards to be specified by School representatives in consultation with Estates. [ See CIBSE guide]
20.2 | If CZ is mechanically ventilated there must be an inward flow of air from adjacent areas into the CL. This may be achieved by extract volume removing great volume of air that delivered [ e.g. supply 90% of extract]
20.3 | CZ must not become positively pressured with respect to surrounding areas. Extract systems to be interlocked to supply system to prevent supply system operating in event of extract failure
20.4 | Supply inlets and extract points to be positioned
to ensure maximum mixing and dilution
to avoid compromising performance of MSCs & FCs
20.5 | All air extracted from CZ to be exhausted direct to atmosphere. Location of extract terminal to be such that there is no recirculation of extracted air into the supply system.
21 | VALIDATION
21.1 | Architect to confirm that all aspects of this specification that have been included in the design of the building have met deign criteria on installation
21.2 | Contractor to provide commissioning data to confirm ventilation system operated in accordance with the design specification.
21.3 | Independent certification required to demonstrate performance to the BS of
Autoclaves
Macs
FRCS
Any other specified equipment
To be witnessed by a competent representative of the School /University

## Documents & Standards
Documents and standards
Title | Organisation/Ref | ISBN | Available at
The Management design and operation of microbiological laboratories | HSE -ACDP | ISBN 978 0 7176 2034 0 | http://www.hse.gov.uk/pubns/priced/microbiologyiac.pdf
Biological agents - managing the risk in laboratories and healthcare premises | HSE ACDP [ +DoH & DEFRA] | N/A | http://www.hse.gov.uk/biosafety/biologagents.pdf
Biotechnology - Labs for research etc. Containment levels etc | BS EN 12128:1998 | N/A | British Standards Institute**
Laboratory furniture - recommendations for design and installation | BS EN 14056:2003 | N/A | British Standards Institute**
Microbiological safety cabinets - siting & use etc | BS 5726:2005 | N/A | British Standards Institute**
Microbiological safety cabinets - performance criteria | BS EN 12469 : 2000 | N/A | British Standards Institute**
Autoclaves | BS EN 12347 : 1998 & BS 2646 | N/A | British Standards Institute**
Security Standards for Laboratories | Part 7 Anti Terrorism Crime & Security Act 2011